## CalcSheet
Fluid Properties: | Fluid Type = | Hydrocarbon |  | Norm. Flow (kg/s) = | 2.78 |  | Name: Ian Cameron
| Temperature (°C) = | 65 |  | Max Flow (kg/s) = | 3.336 | (1.2*Norm) | Date: 25/04/00 |  | Sheet:1 | of | 1
| Density (kg/m³) = | 1306 |  |  |  |  | Project: Hydrocarbon Processing System
| Viscosity (mPas) = | 0.9 |  | centipoise
| Suction Side (s) | [5 empty] | Discharge side (d)
| Line size DN (mm) | 40 | I.D. (mm) = | 40.94 |  |  | Line size DN (mm) | 40 | I.D. (mm) = | 40.94
|  |  | Normal | Max | Units |  |  |  | Normal | Max | Units
u=flow/(dens*area) | [1s] Velocity |  | 1.617 | 1.9404 | m/s |  | [1d] Velocity |  | 1.617 | 1.9404 | m/s
Δf (Genereaux) | [2s] Friction loss |  | 1.0408 | 1.4557 | kPa/m |  | [2d] Friction loss |  | 1.0408 | 1.4557 | kPa/m
L | [3s] Line length |  | 3.4 |  | m |  | [3d] Line length |  | 44.5 |  | m
ΔfL = [2s]*[3s] | [4s] Line loss |  | 3.5387 | 4.9492 | kPa |  | [4d] Line loss |  | 46.3152 | 64.7765 | kPa
| [5s] Head losses | (Ki) |  |  |  |  | [5d] Head losses | (Ki)
=[5s]*ρu²/2*10-3 | entrance | 1 | 1.7074 | 2.4587 | kPa | =[5d]*ρu²/2*10-3 | entrance | 0 | 0 | 0 | kPa
| elbows | 0.35 | 0.5976 | 0.86055 |  |  | elbows | 2.1 | 3.5856 | 5.1633
| valves | 0.17 | 0.29027 | 0.41798 |  |  | valves | 0.51 | 0.8708 | 1.2539
| equipment |  | 0 | 0 |  |  | equipment | 0 | 0 | 0
| exit |  | 0 | 0 |  |  | exit | 0 | 0 | 0
| other |  | 0 | 0 |  | Sum Ki | [6d] Total Ki | 2.61 | 4.4564 | 6.4173
Sum Ki | [7s] Total Ki | 1.52 | 2.5953 | 3.7372 |  |  | [7d] Control valve loss |  | 140 | 201.6 | kPa
| [8s] Other losses |  |  |  | kPa |  | [8d] Other losses |  | 85 | 122.4 | kPa
=[4s]+[8s]+[9s] | [9s] Total losses |  | 6.134 | 8.6865 | kPa | =[4d]+[6d]+[7d]+[8d] | [9d] Total losses |  | 275.7717 | 395.1937 | kPa
z | [10s] Static liquid head |  | 1.5 |  | m | z | [10d] Static liquid head |  | 6.5 |  | m
ρgz | [10s*] Static pressure head |  | 19.2178 | 19.2178 | kPa | ρgz | [10d*] Static pressure head |  | 83.2771 | 83.2771 | kPa
| [11s] Equipment pressure |  | 100 | 100 | kPa |  | [11d] Equipment pressure |  | 200 | 200 | kPa
=[10s*]+[11s] | [12s] Total |  | 119.2178 | 119.2178 | kPa | =[10d*]+[11d] | [12d] Total |  | 283.2771 | 283.2771 | kPa
=[12s]-[9s] | [13s] Suction pressure |  | 113.0838 | 110.5313 | kPa | =[12d]+[9d] | [13d] Discharge pressure |  | 559.0488 | 678.4708 | kPa
| [14s] Vapour pressure |  | 0.1 |  | kPa | =[13d]-[13s] | [14d] Differential pressure |  | 445.965 | 567.9395 | kPa
=[13s]-[14s] | [15s] NPSHA |  | 112.9838 | 110.4313 | kPa |  | [14d*] Differential head |  | 34.8088 | 44.3292 | m
[6 empty] | =m.dP/e.rho | Pump shaft power |  | 1.3561 | 1.7271 | kW
[15s]/ρg*1*103 | [16s] NPSHA liquid head |  | 8.8187 | 8.6195 | m | =[6d]/[9d] | Control valve % of total loss |  | 50.7666 |  | %

## Pipe Data
Pipeline Data - Diameters and Wall Thicknesses (mm) ANSI B36.10
|  | Carbon Steel Pipe | [5 empty] | Stainless Steel Pipe
|  |  | Pipe Schedule | [5 empty] | Pipe Schedule
DN (mm) | O.D. (mm) | 40 |  | 80 |  | 160 |  | 5S |  | 10S |  | 40S |  | 80S
|  | wall | I.D. | wall | I.D. | wall | I.D. | wall | I.D. | wall | I.D. | wall | I.D. | wall | I.D.
15 | 21.3 | 2.77 | 15.76 | 3.73 | 13.84 | 4.78 | 11.74 | 1.65 | 18 | 2.11 | 17.08 | 2.77 | 15.76 | 3.73 | 13.84
20 | 26.7 | 2.87 | 20.96 | 3.91 | 18.88 | 5.56 | 15.58 | 1.65 | 23.4 | 2.11 | 22.48 | 2.87 | 20.96 | 3.91 | 18.88
25 | 33.4 | 3.38 | 26.64 | 4.55 | 24.3 | 6.35 | 20.7 | 1.65 | 30.1 | 2.77 | 27.86 | 3.38 | 26.64 | 4.55 | 24.3
40 | 48.3 | 3.68 | 40.94 | 5.08 | 38.14 | 7.14 | 34.02 | 1.65 | 45 | 2.77 | 42.76 | 3.68 | 40.94 | 5.08 | 38.14
50 | 60.3 | 3.91 | 52.48 | 5.54 | 49.22 | 8.74 | 42.82 | 1.65 | 57 | 2.77 | 54.76 | 3.91 | 52.48 | 5.54 | 49.22
80 | 88.9 | 5.49 | 77.92 | 7.62 | 73.66 | 11.13 | 66.64 | 2.11 | 84.68 | 3.05 | 82.8 | 5.49 | 77.92 | 7.62 | 73.66
100 | 114.3 | 6.02 | 102.26 | 8.56 | 97.18 | 13.49 | 87.32 | 2.11 | 110.08 | 3.05 | 108.2 | 6.02 | 102.26 | 8.56 | 97.18
125 | 141.3 | 6.55 | 128.2 | 9.53 | 122.24 | 15.88 | 109.54 | 2.77 | 135.76 | 3.4 | 134.5 | 6.55 | 128.2 | 9.52 | 122.26
150 | 168.3 | 7.11 | 154.08 | 10.97 | 146.36 | 18.26 | 131.78 | 2.77 | 162.76 | 3.4 | 161.5 | 7.11 | 154.08 | 10.97 | 146.36
200 | 219.1 | 8.18 | 202.74 | 12.7 | 193.7 | 23.01 | 173.08 | 2.77 | 213.56 | 3.76 | 211.58 | 8.18 | 202.74 | 12.7 | 193.7
250 | 273.1 | 9.27 | 254.56 | 12.7 | 247.7 | 28.58 | 215.94 | 3.4 | 266.3 | 4.19 | 264.72 | 9.27 | 254.56 | 12.7 | 247.7
300 | 323.9 | 9.53 | 304.84 | 12.7 | 298.5 | 33.32 | 257.26 | 3.96 | 315.98 | 4.57 | 314.76 | 9.52 | 304.86 | 12.7 | 298.5
400 | 406.4 | 9.53 | 387.34 | 12.7 | 381 | 40.49 | 325.42 | 4.19 | 398.02 | 4.78 | 396.84
500 | 508 | 9.53 | 488.94 | 12.7 | 482.6 | 50.01 | 407.98 | 4.78 | 498.44 | 5.54 | 496.92
600 | 610 | 9.53 | 590.94 | 12.7 | 584.6 | 59.54 | 490.92 | 5.54 | 598.92 | 6.35 | 597.3
700 | 711 | 9.53 | 691.94 | 12.7 | 685.6
800 | 813 | 9.53 | 793.94 | 12.7 | 787.6
900 | 914 | 9.53 | 894.94 | 12.7 | 888.6

## Head Loss Data
Head Loss Data for Valves and Fittings
(Hydraulic Institute, 1961; Perry 4th Edn Table 5-19)
Pipeline fittings | Equivalent number of velocity heads, Ki (u2/2g)
Average
Flanged 45 deg regular elbow | 0.35
Flanged 45 deg long elbow | 0.2
Flanged 90 deg regular elbow | 0.35
Flanged 90 deg long elbow | 0.25
Flanged 180 deg regular bend | 0.35
Flanged 180 deg long bend | 0.25
Pipe inlet | 1
Square edged inlet | 0.5
Bell shaped inlet | 0.05
Flanged Tee - through flow | 0.16
Flanged Tee - branch flow | 0.7
Gate valve - open | 0.17
Gate valve - 3/4 open | 0.9
Gate valve - 1/2 open | 4.5
Gate valve - 1/4 open | 24
Globe valve - open | 6.4
Globe valve - 1/2 open | 9.5
Diaphragm valve - open | 2.3
Diaphragm valve - 3/4 open | 2.6
Diaphragm valve - 1/2 open | 4.3
Diaphragm valve - 1/4 open | 21
Angle valve -open | 3
Butterfly valve - 5 deg | 0.24
Butterfly valve - 10 deg | 0.52
Butterfly valve - 20 deg | 1.54
Butterfly valve - 40 deg | 10.8
Butterfly valve - 60 deg | 118
Check valve - swing | 2
Strainer - basket | 1.2